## Slide 1
Fast Salt System | Rankine power cycle
Selected preliminary design • 5 kPa condenser reference case
1,500 MW thermal → 679 MW gross electric | 45.2% gross efficiency
Steam
generators
(3 × 500 MWt)
HP
Steam
reheater
IP
LP
HP turbine
Reheat turbine
LP turbine
Main steam
24 MPa • 557°C
711.7 kg/s
Heating branch
187.0 kg/s
2.8 MPa
253°C
2.66 MPa
510°C
415.3 kg/s
0.60 MPa
308°C
253 MW reheat
LP exhaust
5 kPa • 33°C
9.0% moisture
WISTR
P
Salt
602°C
537°C
Coolant pump
G
G
Condenser
804 MW rejected
Cooling water
19.8 → 27.9°C
23.8 m³/s
Heating return → HP4
24 MPa • 380°C¹
Feed-pump
turbine
From HP: 7.64 MPa / 378°C
21.4 MW shaft
Exhaust
0.60 MPa
Cond. pump
Feed pump
Deaerator
0.60 MPa
159°C
HP4
287°C
HP + RH¹
7.64 MPa
HP3
225°C
HP exhaust
2.80 MPa
HP2
196°C
Pump turbine
1.60 MPa
HP1
175°C
Pump turbine
1.00 MPa
LP3
107°C
0.155 MPa
LP2
95°C
0.100 MPa
LP1
64°C
0.030 MPa
Feedwater → SG
24 MPa • 287°C
24 MPa
163°C
0.72 MPa
33°C
HP feedwater heaters
LP feedwater heaters
LP turbine bleeds
Water outlet temperatures shown below heaters
Steam
Water
Heating / extraction
Pressures absolute • Gross output; net auxiliaries pending
¹ Heating return throttles into HP4. Heater drains cascade to deaerator (HP) / condenser (LP); small lines summarized.
Notes: Fast Salt System — preliminary Rankine cycle, 11 October 2026. Layout redrawn from Thomas J. Wielenga's supplied Diagram.pdf (23 April 2025), /Users/thomaswielenga/Documents/Ideas/Nuclear Reactor/Steam Generator/graphics/Diagram.pdf. Calculated states: /Users/thomaswielenga/Documents/dev/fastSalt/calculations/power-cycle/reheat-selection.json, selected_at_5kPa. SHA-256: eda8391e0fef20ae71c36a711a8f8fc8142972914360429a6b1b6119fb9be455. Official calculation commentary: calculations/power-cycle/Selected reheat and wetness - Hurmet.md. All pressures absolute. The 5 kPa reference, not the coupled 20°C cooling case, is used consistently. Main steam 711.670 kg/s, heating branch 187.006 kg/s, hot reheat 415.329 kg/s, LP exhaust 361.044 kg/s. Gross 678.723 MW (45.248%); no net power claim. Feed-pump turbine shaft 21.435 MW is already allowed in the cycle flow calculation. Reheater minimum approach 20.276 K. HP exhaust 2.8 MPa/253°C becomes 2.66 MPa/250.7°C after the reheater inlet loss. Heating fluid remains at 24 MPa until throttled into HP4; it is not an isothermal condensing stream. LP moisture is equilibrium exhaust moisture, not a supplier wetness guarantee. Condenser reference cooling water 19.820/27.932°C and 23.763 m³/s. SG salt 875/810 K from the inherited generator design. Three SG represented in aggregate. HP/IP and LP generator symbols preserve the source schematic, not a selected shaft-line design. Bleed and drain lines are summarized: HP4 at7.644 MPa also takes heating return; HP3 at2.8 MPa; HP2/HP1 at1.6/1.0 MPa from feed pump turbine; its0.6 MPa exhaust supplies deaerator. LP3/2/1 at0.155246/0.1/0.03 MPa. HP drains cascade4→3→2→1→DA; LP drains3→2→1→condenser. Feedwater pressure losses other than modeled pumps are not yet resolved. Preliminary performance and equipment arrangement; supplier verification pending.