## Slide 1
Fast Salt System | Rankine power cycle
Motor-driven boiler feed pump • Preliminary cycle at 5 kPa condenser pressure
1,500 MW thermal → 697.1 MW gross | 671.6 MW after BFP + condensate pumps*
Steam
generators
(3 × 500 MWt)
HP
turbine
Steam
reheater
Reheat
(IP)
LP
turbine
Main steam
24 MPa • 557°C
711.7 kg/s
Heating branch
208.6 kg/s
2.8 MPa
253°C
2.66 MPa
510°C
463.2 kg/s
0.60 MPa
308°C
282 MW reheat
LP exhaust
5 kPa • 33°C
9.0% moisture
WISTR
P
Salt
602°C
537°C
Coolant pump
G
G
Condenser
809 MW rejected
Cooling water
19.7 → 27.9°C
23.8 m³/s
24 MPa / 380°C¹
25.0 MW electric
M
BFP motor
23.7 MW shaft
Cond. pump
Feed pump
Deaerator
0.60 MPa
159°C
HP4
287°C
7.64
MPa
HP3
225°C
2.80
MPa
HP2
196°C
1.60
MPa
HP1
175°C
1.00
MPa
LP3
100°C
0.122
MPa
LP2
95°C
0.100
MPa
LP1
64°C
0.030
MPa
Feedwater → SG
24 MPa • 287°C
26.5 MPa
163°C
1.0 MPa
33°C
HP feedwater heaters
LP feedwater heaters
Steam
Water
Heating / extraction
Pressures absolute • *Other station loads excluded
Dots = junctions; bridges = crossings. ¹ Return throttles into HP4. Drains cascade to deaerator (HP) / condenser (LP), not drawn.
Notes: Fast Salt System — motor-driven boiler feed pump alternative, 11 October 2026. Layout adapted from the prior editable cycle diagram, originating with Thomas J. Wielenga's supplied Diagram.pdf (23 April 2025). Source: /Users/thomaswielenga/Documents/dev/fastSalt/calculations/power-cycle/bfp-drive-comparison.json, proposed_pressure_comparison.electric, SHA-256 8c4b58352f462978f624f7b458e67b1e25122fee611ecb87cb70b12b5f2c3b79. Original common state source: /Users/thomaswielenga/Documents/dev/fastSalt/calculations/power-cycle/reheat-selection.json, SHA-256 eda8391e0fef20ae71c36a711a8f8fc8142972914360429a6b1b6119fb9be455. Cooling envelope: /Users/thomaswielenga/Documents/dev/fastSalt/calculations/power-cycle/cooling-cases.json, SHA-256 32fd8be3088d9b5aa524099a49a3020161819c29b404022b83f28185006417ac. Official calculation: calculations/power-cycle/BFP drive comparison - Hurmet.md. All pressures absolute. Main flow 711.6702463557692 kg/s; gross 697.0852550532251 MW; BFP 23.70997211455103 MW shaft and 24.95786538373793 MW electrical, assumed combined drive efficiency 95%; condensate pump 0.5373064266346954 MW electrical; remainder 671.5900832428524 MW excludes all other station loads. This is not final net export. BFP discharge 26.5 MPa; modeled pressure budget is dissipated after the HP heaters before the SG inlet at 24 MPa / 286.85°C. Condensate discharge 1.0 MPa. The aggregate BFP symbol represents the two duty units in a 3 x 50% arrangement, with a provisional 15 MW motor shaft allowance for each. It is no longer driven by a steam turbine. HP2/HP1 receive 1.6/1.0 MPa bleeds from the main IP expansion, at 434.5192359658515/370.8416485278791°C, 13.482481796001286/4.54259056822167 kg/s; DA receives 32.56737529345633 kg/s from the 0.6 MPa IP outlet. LP3 pressure 0.12185545090776068 MPa closes the matched steam-drive reference at the larger pump duty and is retained here. Reheater duty 281.6211467468419 MW, heating branch 208.56566467595448 kg/s, reheated flow 463.2104595237085 kg/s. Reheater minimum approach 20.275955851518574 K. Condenser heat 809.3765271411932 MW at exactly 5 kPa, LP moisture 8.96889556225634%. The shown cooling water 19.73508993343261/27.899703770704168°C with 23.763375654778333 m3/s is consistent with that exact pressure and the retained condenser UA, not the separate coupled 20°C case. HP drains cascade 4→3→2→1→DA; LP drains 3→2→1→condenser; drains not drawn. Reheater heating return stays at 24 MPa / 380°C until throttled into HP4. Shaft/generator grouping preserves the earlier conceptual schematic; it is not a selected mechanical arrangement. Native editable objects; no flattened diagram. This presentation of the alternative does not select equipment or establish startup/transient capability.